## Slide 1
Power Supplies Group
Laurent JOLLY
ASD Workshop
24 January 2023

## Slide 2: Presentation Outline
Operation - Reliability of SR PS
Review of PSG Projects
HQPS Black Out Protection

## Slide 3: Storage Ring PS Reliability
Chart: Power Supplies monthly failure rate
| 43831 | 43862 | 43891 | 43922 | 43952 | 43983 | 44013 | 44044 | 44075 | 44105 | 44136 | 44166 | 44197 | 44228 | 44256 | 44287 | 44317 | 44348 | 44378 | 44409 | 44440 | 44470 | 44501 | 44531 | 44562 | 44593 | 44621 | 44652 | 44682 | 44713 | 44743 | 44774 | 44805 | 44835 | 44866 | 44896
Common Source | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 1
STATUM PS | 4 | 3 | 1 | 4 | 0 | 5 | 8 | 8 | 3 | 3 | 3 | 0 | 0 | 0 | 1 | 4 | 4 | 4 | 1 | 2 | 8 | 1 | 0 | 0 | 0 | 4 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 6 | 2
MOSplates | 1 | 1 | 1 | 1 | 2 | 2 | 1
SF/SD Corrector PS | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1
SH Corrector PS | 1 | 2 | 5 | 2 | 2 | 2 | 4 | 3 | 3 | 1
 | MTBF [h] |  | 
 | Y2020 | Y2021 | Y2022
10 x CS 360V and CS 48V | 900 | 6792 | 2224
864 x Main PS (STATUM) | 111 | 271 | 351
32 x Hotswap (MOSplates)* | N/A | 750 | >6672
864 x SF/SD Corr PS | 1350 | 2264 | 3336
294 x SH Corr PS | 216 | >6792 | >6672
Whole System | 64 | 178 | 277
2021
2020
2022
* Hotswap hardware installed but automatic swap function not operational
23 failures in Y22 (USM + MDT + Shutdown restart), average 2 per month
MTBF for the overall system in Y22 increased by 50% versus Y21
65% of failures are embedded software related
Other less visible problems: overheating power connections in HSC, waterleaks
Prediction for 2023?
Chart: 
| CS | STATUM | SF/SD Corr
 | 3 | 18 | 2

## Slide 4: TL2 Corrector PS revamping project
Project Status
  Cubicle design and construction
    Strong focus on project doc (system specifications, elec and mech drawings)
    Cubicle assembly and wiring done in house. Fully Completed.
  Control software
    PLC software completed at 50%
    Functional specifications for TANGO device server implementation not started
Main People involved: P. Falaise, L. Jolly, S. Lagarde, P. Sallamand

## Slide 5: STATUM test and repair Lab (MD-0-16)
Full SRPS System Test stand (CS + HSC + Magnets + TANGO control)
  Used extensively for Hotswap development work
  For validation test of STATUM firmware modifications
Repair station
  Manufactured and tested 265 electronic boards (stock of spare parts)
  Repaired 12 STATUM PS and 2 electronic boards in Y22
STATUM Calibration platform
  Routine calibration of STATUM PS after repair
  Future periodic calibration campaign for 862 PS?
Main People involved: A. Thai, S. Lagarde, M. Michel, B. Joly (+ PSG and TID)

## Slide 6: Hotswap STATUS
Activities of last 12 months
Jan – Sept 22: Developed the TANGO controls and user interface Improved robustness of system
Sept – Oct 22: activation in the SR during MDTs only (at night)
Nov 22: partial deployment in USM (2-3 weeks in 8 cells)
17th Jan 23: full deployment in USM
What’s next:
  assess reliability of the system in USM and fix arising issues
  Improves user-interface for operators (automatic turn-off / turn-on when beam is on/off)
  Y24: Equip sextupole magnets with MOSplates

## Slide 7: A peak at Hotswap System complexity
33 x PS Current Setpoints
Hot-Swap + MOSplate
Manager
TANGO
27x Running PS
6x Standby PS
33 x PS Current Setpoints
27 x Magnet Current
Measurements
7 x MOSplates
84 x Power Switch
Commands
27x Magnets
Hotswap system status
7 pieces of embedded software (DSP, ucontroller, FPGA) + 4 TANGO DS to control the system!
>10 people involved in the project these last 3 years with high turnover:
  JF Bouteille, M. Di Vito, P. Falaise, A. Thai (PSG)
  R Biv, A. Broquet, C. Hervé, L. Siron (ISDD-EU)
  J.L. Pons, M. Taurel, A. Valiente (ACU).

## Slide 8: Other Ongoing PRojects
STATUM firmware improvement (O. Goudard, M. Di Vito):
  Added features for facilitating maintenance / fault diagnosis.
  Consolidated the code (software maintenability)
Upgrade of RIPS embedded control system (S. Lagarde + L. Siron)
  Regain knowledge on the current software eco-system (DSP + FPGA + TANGO DS)
  Switch to a new DANCE control platform (Y23)
  Improve RIPS current regulation performance (Y24?)

## Slide 9: HQPS Simplified Architecture
Reactors: barrier (high impedance) against HF disturbances coming from utility grid
Rotablocks (14 off):
Combination of a
Low impedance alternator (clean sinewave voltage source)
Kinetic energy accumulator
Diesel Engine Generator (1 off):
Able to supply 1000kW for long period of time in case of black-out on utility grid

## Slide 10: Protection against Utility Black Out (1/2)
1- Normal operation (utility grid OK)
HQPS alternators do not provide any active power
2 - Suddenly a fault occurs on utility grid in the neighborhood =>This causes a large voltage dip upstream HQPS
3 - Automatic disconnection of HQPS from the utility grid => HQPS’s accumulators powering ESRF
=> Accumulator running out of kinetic energy => Load shedding of heavy consumers
4 – After long time utility grid voltage is still NOT back to normal condition

## Slide 11: Protection against Utility Black Out (2/2)
=> Accumulator running out of kinetic energy => Load shedding of heavy consumers to avoid blackout extending to ESRF
4 – After long time utility grid voltage is still NOT back to normal condition
5 – Diesel engine starts and accelerate to 1500rpm in 25s
6 – Generator connects to 20kV network and takes all the load
=> Can run continuously in such conditions till blackout recovery from utility grid

## Slide 12: Special Thanks to the PSG TEAM
S. Lagarde
O. Goudard
P. Falaise
A. Thai
P. Vidal
P. Sallamand
M. Michel
L. Jolly
M. Di Vito

## Slide 13: Many thanks for your attention